## 1. HVAC
BERTRAMS MECHANICAL SERVICES
SCHEDULE OF QUANTITIES
SCHEDULE NO 1: AIR CONDITIONING AND VENTILATION SYSTEM
PAYMENT
REFERS | ITEM |  |  |  | UNIT | QUAN- | RATE | AMOUNT
TO | NO |  |  |  |  | TITY
| 1.00 | AIR CONDITIONING SYSTEM
Tenderered rates for the following items to be inclusive of all
external connections to drainage, water piping, building works.
| 1.01 | .01 | Supply, install and commission a VRV
(variable refrigerant volume) system that
complies with approved standard specification
complete with all accessories
required to make the installation complete,
including all associated building works, rigging
and making good.
The 3 VRV systems shall comprise of the following:
|  |  | .01 | Condensing unit (heat recovery, 3-pipe
system) with cooling capacity of
67,2 kW. The unit shall have a minimum
Coefficient of Performance of 4,23 and
|  |  |  | Energy Efficiency Ratio of 3.86 | No | 4
|  |  | .02 | Condensing unit (heat recovery, 3-pipe
system) with cooling capacity of
61,6 kW. The unit shall have a minimum
Coefficient of Performance of 4,35 and
|  |  |  | Energy Efficiency Ratio of 3.92 | No | 2
|  |  | .03 | Condensing unit (heat recovery, 3-pipe
system) with cooling capacity of
39,2 kW. The unit shall have a minimum
Coefficient of Performance of 4,82 and
|  |  |  | Energy Efficiency Ratio of 4,52 | No | 1
|  |  | .04 | Condensing unit (heat recovery, 3-pipe
system) with cooling capacity of
33,6 kW. The unit shall have a minimum
Coefficient of Performance of 4,91 and
|  |  |  | Energy Efficiency Ratio of 4,43 | No | 1
|  |  | .05 | 36000 Btu (10,6kW) ceiling cassette indoor unit | No. | 10
|  |  | .06 | 30000 Btu (8,2kW) ceiling cassette indoor unit | No. | 10
|  |  | .07 | 24000 Btu (7.1kW) ceiling cassette indoor unit | No. | 11
|  |  | .08 | 18000 Btu (5,3kW) ceiling cassette indoor unit | No. | 14
|  |  | .09 | 18000 Btu (5.3 kW) midwall split indoor unit | No. | 19
|  |  | .10 | 12000 Btu (3.6kW) midwall split indoor unit | No. | 8
|  |  | .11 | 9000 Btu (2.6kW) midwall split indoor unit | No. | 14
| CARRIED FORWARD | [6 empty] | 0
| BROUGHT FORWARD | [6 empty] | 0
|  | .02 | Supply and install refrigerant piping of the
following sizes for the above VRV system:
The rate shall be inclusive of all connection wiring,
trunking, insulation, supports and all accessories
required to make the installation complete
The refrigerant piping shall be suitable for R410A gas.
|  |  | .01 | 6.4mm diameter | m | 670
|  |  | .02 | 9.5mm diameter | m | 430
|  |  | .03 | 12.7mm diameter | m | 780
|  |  | .04 | 15.9mm diameter | m | 290
|  |  | .05 | 19.1mm diameter | m | 240
|  |  | .06 | 22.2mm diameter | m | 130
|  |  | .07 | 28.6mm diameter | m | 240
|  |  | .08 | 31.8 mm diameter | m | 36
|  |  | .09 | 34.9mm diameter | m | 110
|  |  | .10 | 38.1 mm diameter | m | 9
|  |  | .11 | 53,9mm diameter | m | 12
|  | 0.3 |  | Supply and recharge VRV systems with
|  |  |  | additional R410A refrigerant charge | kg | 110
|  | 0.4 |  | Supply and install wall mounted remote
|  |  |  | controllers for indoor units | No | 23
|  | 0.5 |  | Supply and install branch selector units for
|  |  |  | indoor piping | sum | 1
|  | 0.6 |  | Supply and install multi connection piping
|  |  |  | kits for all outdoor units | sum | 1
|  | 0.7 |  | Supply and install VRV refnet branch piping kits | sum | 1
|  | 0.8 |  | Supply and install control wiring interconnecting
|  |  |  | outdoor units to indoor units | sum | 1
| 1.02 |  |  | Individual Units
|  |  | .01 | Supply and installation of new 5,3 kW
midwall split inverter type heating and cooling
air-conditioning unit. Rate to be inclusive
of all required building work, pipework and
|  |  |  | making good. (For Server Room) | No. | 0 |  | 0
| CARRIED FORWARD | [6 empty] | 0
| BROUGHT FORWARD | [6 empty] | 0
|  |  | .02 | Supply and installation of new 7,1 kW
midwall split inverter type heating and cooling
air-conditioning unit. Rate to be inclusive
of all required building work, pipework and
|  |  |  | making good. (For Server) | No. | 2
| 1.03 |  |  | Commissioning and Training
|  | 0.1 |  | Test and commissiong entire VRV heat recovery
|  |  |  | system & independent units & handover to client | Sum | 1
|  | 0.2 |  | Issuing of manuals and training of staff about the
VRV air conditioning system and packaged
|  |  |  | units and handover to client. | Sum | 1
| 1.04 | VENTILATION SYSTEM
|  | 0.1 |  | Supply and install 400mm diameter in-line
axial fresh air supply fan supplying 1100 litres
per second at 50 Pa complete with 2 sound
|  |  |  | attenuators, filter box and accessories. | No. | 2
|  | 0.2 |  | Supply and install 315mm diameter in-line
axial fresh air supply fan supplying 720 litres
per second at 90 Pa complete with 2 sound
|  |  |  | attenuators, filter box and accessories. | No. | 1
|  | 0.3 |  | Supply and install 315mm diameter in-line
axial fresh air supply fan supplying 540 litres
per second at 70 Pa complete with 2 sound
|  |  |  | attenuators, filter box and accessories. | No. | 2
|  | 0.4 |  | Supply and install 315mm diameter in-line
axial fresh air supply fan supplying 480 litres
per second at 55 Pa complete with 2 sound
|  |  |  | attenuators, filter box and accessories. | No. | 1
|  | 0.5 |  | Supply and install 315mm diameter in-line
axial fresh air supply fan supplying 380 litres
per second at 60 Pa complete with 2 sound
|  |  |  | attenuators, filter box and accessories. | No. | 2
|  | 0.6 |  | Supply and install 315mm diameter in-line
axial fresh air supply fan supplying 330 litres
per second at 55 Pa complete with 2 sound
|  |  |  | attenuators, filter box and accessories. | No. | 2
|  | 0.7 |  | Supply and install 315mm diameter in-line
axial fresh air supply fan supplying 240 litres
per second at 30 Pa complete with 2 sound
|  |  |  | attenuators, filter box and accessories. | No. | 1
|  | 0.8 |  | Supply and install 300mm diameter axial
wall fresh air supply fan supplying 810 litres
per second at 75 Pa complete with all
|  |  |  | accessories. | No. | 2
| CARRIED FORWARD | [6 empty] | 0
| BROUGHT FORWARD | [6 empty] | 0
|  | 0.9 |  | Supply and install 315 mm diameter in-line
axial extraction air fan extracting 280 litres
per second at 80 Pa complete with 1
|  |  |  | sound attenuator and accessories. | No. | 8
|  | 0.10 |  | Supply and install 315 mm diameter in-line
axial extraction air fan extracting 180 litres
per second at 90 Pa complete with 1
|  |  |  | sound attenuator and accessories. | No. | 3
|  | 0.11 |  | Supply and install 315 mm diameter in-line
axial extraction air fan extracting 140 litres
per second at 40 Pa complete with 1
|  |  |  | sound attenuator and accessories. | No. | 1
|  | 0.12 |  | Supply and install 315 mm diameter in-line
axial extraction air fan extracting 100 litres
per second at 40 Pa complete with 1
|  |  |  | sound attenuator and accessories. | No. | 1
|  | 0.13 |  | Supply and install 225 mm wall extraction fan
|  |  |  | extracting air at 50 litres/sec | No. | 2
|  | 0.14 | Supply and install externally insulated galvanized
600 mm diameter spiral ducting, rate to be complete
|  |  | with all required spigots and mounting accessories. |  | m | 0
|  | 0.15 | Supply and install externally insulated galvanized
500 x 250 mm spiral ducting, rate to be complete
|  |  | with all required spigots and mounting accessories. |  | m | 50
|  | 0.16 | Supply and install externally insulated galvanized
400 x 250 mm ducting, rate to be complete
|  |  | with all required spigots and mounting accessories. |  | m | 50
|  | 0.17 | Supply and install externally insulated galvanized
350 x 250 mm spiral ducting, rate to be complete
|  |  | with all required spigots and mounting accessories. |  | m | 230
|  | 0.18 | Supply and install uninsulated galvanized 400mm
diameter spiral ducting, rate to be complete with all
|  |  | required spigots and mounting accessories. |  | m | 0
|  | 0.19 | Supply and install externally insulated galvanized
200mm spiral ducting, rate to be complete with all
|  |  | required spigots and mounting accessories |  | m | 0
|  | 0.20 | Supply and install 300 x 250mm externally insulated
|  |  | galvanized ducting c/w supports and transition pieces |  | m | 100
|  | 0.21 | Supply and install 250 x 250mm externally insulated
|  |  | galvanized ducting c/w supports and transition pieces |  | m | 220
|  | 0.22 | Supply and install 250 x 200mm externally insulated
|  |  | galvanized ducting c/w supports and transition pieces |  | m | 30
| CARRIED FORWARD | [6 empty] | 0
| BROUGHT FORWARD | [6 empty] | 0
|  | 0.23 | Supply and install 200 x 200mm externally insulated
|  |  | galvanized ducting c/w supports and transition pieces |  | m | 52
|  | 0.24 | Supply and install 350 x 350mm uninsulated
|  |  | galvanized ducting c/w supports and transition pieces |  | m | 30
|  | 0.25 | Supply and install 300 x 250mm uninsulated
|  |  | galvanized ducting c/w supports and transition pieces |  | m | 20
|  | 0.24 | Supply and install 250 x 250mm uninsulated
|  |  | galvanized ducting c/w supports and transition pieces |  | m | 180
|  | 0.25 | Supply and install 250 x 200mm uninsulated
|  |  | galvanized ducting c/w supports and transition pieces |  | m | 6
|  | 0.26 | Supply and install 200 x 200mm uninsulated
|  |  | galvanized ducting c/w supports and transition pieces |  | m | 6
|  | 0.27 | Supply and install uninsulated galvanized 250mm
diameter spiral ducting, rate to be complete with all
|  |  | required spigots and mounting accessories. |  | m | 6
|  | 0.28 | Supply and install insulated galvanized 150mm
diameter spiral ducting, rate to be complete with all
|  |  | required spigots and mounting accessories. |  | m | 420
|  | 0.29 | Supply and install uninsulated galvanized 150mm
diameter spiral ducting, rate to be complete with all
|  |  | required spigots and mounting accessories. |  | m | 16
|  | 0.30 | Supply and install 150 x 200mm diameter
|  |  | galvanized ducting c/w supports and transition pieces. |  | m | 6
|  | 0.31 | Supply and install uninsulated 150mm flexible
ducting, rate to be complete with all installation
|  |  | accessories |  | m | 80
|  | 0.32 | Supply and install 150mm disc valve |  | No. | 8
|  | 0.33 | Supply and install 500mm x 300mm natural
|  |  | anodised alumimium door grille. |  | No. | 32
|  | 0.34 | Supply & install 300 x 250 mm fire dampers
|  |  | with fusible links |  | No. | 45
|  | 0.35 | Supply 500mm x 500mm natural anodised
|  |  | aluminium supply air grille. |  | No. | 110
|  | 0.36 | Supply 1200mm x 600mm natural anodised
|  |  | aluminium return air grille. |  | No. | 2
| CARRIED FORWARD | [6 empty] | 0
| BROUGHT FORWARD | [6 empty] | 0
|  | 0.37 | Supply 350mm x 350mm natural anodised
|  |  | aluminium weather louvre. |  | No. | 30
|  | 0.38 | Supply 300mm x 300mm natural anodised
|  |  | aluminium weather louvre. |  | No. | 4
|  | 0.39 | Supply 250mm x 250mm natural anodised
|  |  | aluminium weather louvre. |  | No. | 2
|  | 0.40 | Supply and install 300mm x 300mm white
|  |  | epoxy coated supply air grille, 150mm spigot. |  | No. | 160
|  | 0.41 | Supply and install 150mm x 150mm white
|  |  | epoxy coated supply air grille, 150mm spigot. |  | No. | 2
|  | 0.42 |  | Supply and install 25mm PVC piping for
|  |  |  | condensate removal including all accessories. | m | 1350
|  | 0.43 | Provide insulation for underside of slabs |  | PC | Sum | 200000 | 200000
Smoke Extraction
Supply and install smoke extraction system as per
|  |  | Fire Engineer's Specifications |  | PC | Sum | 1521000 | 1521000
| 1.05 |  |  | Commissioning and Training
|  | 0.1 |  | Prepare and supply three sets of
detailed Operation and Maintenance Manuals
including as-built drawings. An electronic
version of the drawings shall also be supplied
on compact disc in AutoCAD format. The
manuals and compact disc shall be handed
|  |  |  | over to the Engineer. | - | - | Sum
Development of a syllabus for maintenance
and operations training
|  | 02 | HVAC Systems |  | - | - | Sum
Presentation of training course on HVAC
Equipment Maintenance and Operations.
|  | 03 | HVAC System |  | - | - | Sum
COMMISSIONING
Commissioning and testing of the installation
|  | .01 | HVAC Equipment |  | - | - | Sum
| CARRIED FORWARD TO SUMMARY | [6 empty] | 1721000

## 2 Wet
BERTRAMS MECHANICAL SERVICES
BILL NO 2
BUILDING WET SERVICES
PAYMENT
REFERS | ITEM |  |  | DESCRIPTION | UNIT | QUAN- | RATE | AMOUNT
TO | NO |  |  |  |  | TITY
| 2.00 | PLUMBING
| 2.01 | Installation of domestic
copper water piping systems,
Class 0 SABS 460 with capillary
copper fittings :
|  | .01 | Cold water piping installed on surface
in ducts, against walls and soffits
including bracketing
|  |  | .01 | 35 dia | m | 10
|  |  | .02 | 28 dia | m | 120
|  |  | .03 | 22 dia | m | 210
|  |  | .04 | 15 dia | m | 280
|  | .02 | Hot water piping , installed on surface
in ducts, against walls and soffits,
inclusive of lagging , cladding and
bracketing
|  |  | .01 | 22 dia | m | 130
|  |  | .02 | 15 dia | m | 270
|  | .03 | Hot and cold water piping chased in
walls including wrapping of pipes
with builders paper, chasing and
reinstatement of chased surfaces
|  |  | .03 | 22 dia | m | 70
|  |  | .04 | 15 dia | m | 220
|  | .04 | Capillary soldered copper fititings
for tees;
|  |  | .01 | 22 dia | No | 240
|  |  | .02 | 15 dia | No | 340
|  |  | .03 | 28 dia x 22 dia | No | 80
|  |  | .03 | 22 dia x 15 dia | No | 90
|  | .05 | Capillary soldered copper fittings
for elbows
|  |  | .01 | 22 dia | No | 270
|  |  | .02 | 15 dia | No | 240
| Carried forward | [5 empty] | R | 0
| Brought forward | [5 empty] | R | 0
|  | .06 | Shut off ball valves
|  |  | .01 | 20 dia | No | 120
|  |  | .02 | 15 dia | No | 390
|  | .07 | Strainers
|  |  | .01 | 25 dia | No | 60
|  |  | .02 | 20 dia | No | 52
|  | .08 | Non return valves
|  |  | .01 | 25 dia | No | 30
|  |  | .02 | 20 dia | No | 120
|  |  | .03 | 15 dia | No | 390
| 2.02 | Supply and install domestic SABS
approved solar geysers including shut-off
valves, strainers, non-return valves
expansion relief valve, safety
valve and 3kW power provision (Indirect system);
|  | .01 | 300 ltr |  | No | 4
|  | .02 | 200 ltr |  | No | 3
|  | .03 | Supply and install 150l electric
geyser complete with all accessories to
|  |  | make installation complete. |  | No | 2
| 2.03 | Supply and installation of a 5l Hydro Boil |  |  | No | 4
| 2.04 | Allow for fittings to connect to main water
|  | pipe |  |  | sum | - | -
| 2.05 | Green Wall Irrigation
|  | .01 | Allow for automatic irrigation of the
|  |  | Greenwall |  | Prov | - | - | 30000
|  | .02 | Profit and attendance |  | % |  | 10% | 3000
| Carried forward | [5 empty] | R | 33000
| Brought forward | [5 empty] | R | 33000
| 2.06 | Supply and installation of water drainage
pipe work and fittings
|  | .01 | uPVC piping installed on surface
|  |  | in ducts, against walls and soffits | [5 empty] | 0
including bracketing
|  |  | .01 | 110 dia | m | 540
|  |  | .02 | 50 dia | No | 330
|  | .02 | Extra over 50 mm pipes for
|  |  | .01 | Bend | No | 160
|  |  | .02 | Bend with cleaning eye | No | 90
|  |  | .03 | Junction with cleaning eye | No | 60
|  |  | .04 | Vent Fitting with Cowl | No | 150
|  |  | .05 | Butyl resealing P-trap | No | 190
|  |  | .06 | Two way vent valves | No | 50
|  | .03 | Extra over 110 mm pipes for
|  |  | .01 | Bend | No | 54
|  |  | .02 | Bend with cleaning eye | No | 40
|  |  | .03 | Junction with cleaning eye | No | 34
|  |  | .04 | Butyl resealing P-trap | No | 70
|  |  | .05 | Two way vent valve | No | 40
| 2.07 | Allow for fittings to connect to main sewer
|  | pipe |  |  | sum | -
| 2.08 | Tests and Inspection on completion
of installation work
|  | .01 | Pressure test completed water
|  |  | piping installation |  | item | 1
| TOTAL CARRIED FORWARD TO WET SERVICES SUMMARY | [5 empty] | R

## 3 Fire Detection
BERTRAMS MECHANICAL SERVICES
BILL NO. 3
FIRE DETECTION
| ITEM |  |  | DESCRIPTION | UNIT | QUAN- | RATE | AMOUNT
| NO |  |  |  |  | TITY
| 3.0 | FIRE DETECTION SYSTEM
| 3.01 | Supply, install,test and commission a complete
fire detection and alarm system as per
The Fire detection shall comply with SANS10400,
SANS 10139. The fire detection system shall be
provided throughout the facilities (System category
L1 and P) and shall be an addressable Fire
Detection system. Refer to drawings in tender document.
| 3.02 | Supply and install 25mm metal conduits for fire
detection system wiring, including all round and
|  | square termination boxes and P8000 trunking. |  |  | m
| 3.03 | Supply and install fire resistant type 1mm² wire,
interconnected between, the detectors, the
|  | break glass units, strobe light and audible alarm. |  |  | m
| 3.04 | Supply and install 4 loop analogue
addressable fire control panel complete
with battery back-up system and printer as per
specification. Wall mounted 1,5m above ground in
|  | area indicated on the Engineer's drawing. |  |  | No
| 3.05 | Supply and install mimic fire control panel
with battery back-up system and printer as per
|  | Engineer's drawing. |  |  | No
| 3.06 | Supply and install analogue addressable optical
smoke detectors as per specification fixed to a
|  | 65mm diameter conduit box. |  |  | No
| 3.07 | Supply and install analogue addressable rate-of
rise heat detectors as per specification fixed to
|  | a 65mm diameter conduit box. |  |  | No
| 3.08 | Supply and install optical smoke detectors or
rate-of rise heat detectors with base siren/sounder
warning unit as per specification fixed to a 65mm
diameter conduit box, as shown on the
|  | drawing. |  |  | No
| 3.09 | Supply and install fire signage and accessories. |  |  | - | - | Sum
| 3.10 | Supply and install analogue addressable 'Red'
strobe lights as per specification fixed to a 65mm
|  | diameter conduit box. |  |  | No | 36
| 3.11 | Supply and install Red "fire" manual call points
(Breakglass Unit) as per specification fixed to a
|  | 65mm diameter conduit box. |  |  | No | 24
| CARRIED FORWARD | [6 empty] | 0
| BROUGHT FORWARD | [6 empty] | 0
| 3.12 | Install accessories to ensure system is interfaced
with the HVAC and Lift installations so as to
|  | comply with Fire Regulations. |  |  | - | - | Sum
| 3.13 | REMRAD System
Supply and install REMRAD system linked
to fire panel and with wireless communication link
to security and emergency management systems.
Installation to include one year's licence
|  | including maintenance. |  |  | No | 1
| 3.14 | Operation and Maintenance Manuals
|  | .01 | Prepare and supply three sets of detailed and
Operation and Maintenance manuals
including as-built drawings. An electronic
version of the drawings shall also be supplied
on compact disc in AutoCAD format. The
manuals and compact disc shall be
|  |  | handed over to the Engineer. |  | - | - | Sum
Development of a syllabus for maintanance
and operations training
|  | .02 | Complete Fire Detection
|  |  | System |  | - | - | Sum
Presentation of training course on Fire
Detection Equipment
Maintenance and Operations
|  | .03 | Complete Fire Detection System |  | - | - | Sum
| 3.15 | Commissioning
Testing and commissioning of the entire fire
detection system including issuing relevant
|  | installation certificates. |  |  | - | - | Sum
| TOTAL BILL NO 3 - CARRIED TO SUMMARY | [5 empty] | R | 0

## 4 Kitchen Equipment
SCHEDULE OF QUANTITIES: REPAIR WORK
BILL NO 4:
KITCHEN EQUIPMENT
PAYMENT
REFERS | ITEM |  |  | DESCRIPTION | UNIT | QUAN- | RATE | AMOUNT
TO | NO |  |  |  |  | TITY
| 4.00 | GENERAL
| 4.01 | As-built information and Operating and
Maintenance Manuals
|  | .01 | Obtaining of all available information
for updating, compiling and finalising
the three sets of Operating
and Maintenance Manuals including
|  |  | as-built drawings. |  | - | - | Sum
| 4.02 | Training
|  | .01 | Kitchen equipment |  | - | - | Sum
|  | .02 | Development of syllabus for
|  |  | training operators |  | - | - | Sum
|  | .03 | Presenting a training course for
|  |  | operators |  | No. | 1
| 4.03 | KITCHEN EQUIPMENT
Tenderered rates for the following items to
be inclusive of all external connections to
drainage, water or steam piping.
| 4.04 | Gas Stove
|  | .01 | Supply and install 4 open burner gas range
stove with oven. The gas rating should
|  |  | be 118 000 kJ/hr |  | No | 5
| 4.05 | Supply and Installation of New Extract
Canopy for the Gas Stoves
|  | .01 | Kitchen extract ventilation hood of 430
stainless steel of approximate
dimensions 3,600 mm (L) x 1,200 mm (W)
0,9 mm thick with all fittings and complete
with 500 x 500 cycloclean grease
|  |  | filters inluding 220 V35 W LED light. |  | No. | 4
|  | .02 | Axial flow type long casing fans. Diameter
500 mm 4pole 380 V and 0.75 kW
|  |  | pressure of 200 pascals. |  | No. | 4
|  | .03 | 500 mm sound attenuators to keep the
noise level within the area of the
canopy to within 70db including square to
|  |  | round fit conopy & 500mm vertical discharge. |  | No. | 4
|  | .04 | Support steel and all accessories to make
|  |  | installation complete |  | No. | 4
| CARRIED FORWARD | [6 empty] | 0
| BROUGHT FORWARD | [6 empty] | 0
| 4.06 | GAS
|  | .01 | Supply and install 48kg LPG free standing gas
cylinders to be installed in a lockable cage.
LP gas cylinders are to be installed in an upright
position supported and bracketed to prevent fall.
Cylinders to be installed in a lockable cage to
|  |  | Architect's specification. |  | No | 4
|  | .02 | Supply and install a 2000 x 1500 x 600mm LPG
|  |  | cylinder lockable cage. |  | No | 1
|  | .03 | Install dia 22mm 2 way gas selector valve in
the middle of the cylinders linking both gas
|  |  | cylinders. |  | No | 2
|  | .04 | Install 4 off dia 22mm gas isolation valves outside
|  |  | after each gas cylinder |  | No | 2
|  | .05 | Supply and install dia 75mm pvc sleeve which is
required to be laid in under the concrete surface
from the gas cylinders outside to the indoor
|  |  | position of gas stoves |  | m | 2
| 4.06 | Microwave
|  | .01 | Supply and install 55 litre 1000W stainless
|  |  | steel micowave oven. |  | No. | 1
| 4.07 | Stainless steel table
|  | .01 | Supply of stainless steel table with
splashback. Table dimensions:length
|  |  | 1650 mm, height 910 mm & depth 650mm |  | No. | 2
| 4.08 | Baking Oven
|  | .01 | Convection Oven and Steamer
|  |  | .01 | Supply and installation of a 40-pan
Convection Oven with Steamer,
|  |  |  | complete with accessories. | No. | 5
| 4.09 | Refrigerator
|  | .01 | Supply and install 660 litre side by side
refrigerator including ice and water
|  |  | dispenser. |  | No. | 7
| CARRIED FORWARD | [5 empty] | R | 0
| BROUGHT FORWARD | [6 empty] | 0
| 4.10 | Display Refrigerator
|  | .01 | Supply and install 118 litre 1500mm x
470mm x 680 display refrigerator 230 V
50 Hz, 0.417kW with 2 shelves with total
|  |  | empty weight of 90 kg. |  | No. | 2
| 4.11 | Cold Room
|  | .01 | Supply and install 2m x 2,4m x 2,4m cold
room with chromadek polystyrene panels with
1,5 HP condensing unit with matching
|  |  | blower coil. Sinlge phase 25A. |  | No. | 2
| 4.12 | Grease/Fat Trap
|  | .01 | Break out existing brick &
concrete, remove rubble and prepare
|  |  | for construction of new trap chamber |  | No | 3
|  | .02 | Grease trap chamber complete as per
|  |  | drawing for 16l/s grease trap |  | No | 3
|  | .03 | Stainless steel grease trap with a flow
rate of 16l/s, complete with stainless
|  |  | steel covers as per drawing |  | No. | 3
| 4.10 | COMMISSIONING
Commissioning and testing of the
installation:
|  | .01 | Bill No. 4: Kitchen Equipment |  | - | - | sum
| TOTAL BILL NO 4 - CARRIED TO SUMMARY | [5 empty] | R | 0

## 5 Lifts
BERTRAMS: MECHANICAL SERVICES
BILL NO. 5 LIFTS
PAYMENT | ITEM
REFERS | NO |  |  | DESCRIPTION | UNIT | QUAN- | RATE | AMOUNT
TO | [5 empty] | TITY
| 5.00 | LIFTS
| 5.01 | Supply and installation of elevator complete
with accessories
|  | .01 | 630 kg 4 stop lift for Administration Block |  | - | - | Sum
|  | .02 | 1125 kg 4 stop lift for Administration Block |  | - | - | Sum
|  | .03 | Allow for interface with Fire Detection |  | - | - | Sum
| 5.02 | COMMISSIONING
Commissioning and testing of the installation
|  | .01 | Lifts |  | - | - | Sum
| TOTAL BILL NO 4 - CARRIED TO SUMMARY | [5 empty] | R | 0

## MECHANICAL SUMMARY
BERTRAMS MECHANICAL SERVICES
SUMMARY: SCHEDULE OF QUANTITIES: MECHANICAL SERVICES
BILL NO 1: AIR CONDITIONING AND VENTILATION | R | 1721000
BILL NO 2: WET SERVICES | R | 0
BILL NO 3: FIRE DETECTION | R | 0
BILL NO 4: KITCHEN EQUIPMENT | R | 0
BILL NO 5: LIFTS | R | 0
TOTAL OF SCHEDULE OF QUANTITIES: MECHANICAL SERVICES | R | 1721000