## JDA Bertrams
JDA BERTRAMS
FIRE INSTALLATIONS
BILLS OF QUANTITIES
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
SECTION 1
PRELIMINARY & GENERAL
| SUB-TOTAL |  |  |  | 0
SECTION 2
SPRINKLERS
| SUB-TOTAL |  |  |  | 0
SECTION 3
CONVENTIONAL FIRE PROTECTION
| SUB-TOTAL |  |  |  | 0
SECTION 4
ATRIUM SMOKE CONTROL
| SUB-TOTAL |  |  |  | 0
SECTION 4
FIRE SEALING
| SUB-TOTAL |  |  |  | 0
| TOTAL TRANSFERRED TO FORM OF TENDER |  |  |  | 0
SECTION 1
PRELIMINARY & GENERAL ITEMS
1.1 | Nett price for compliance with the Conditions and Special Conditions | Sum | 1 |  | 0
of Contract, and various specifications, which costs are not specifically
covered elsewhere or by unit rates.
1.2 | Prices shall include for all transportation, conveying, delivering, specialised scaffolding, | Sum | 1 |  | 0
unloading, lifting, storage, fabrication, fitting and fixing, including all accessories
related to fixing the equipment.
1.3 | Prices shall exclude VAT but shall include any taxes | Sum | 1 |  | 0
or related costs incurred in the procurement of
equipment.
1.4 | Tenderers are required to scrutinise the drawings and take the | Sum | 1 |  | 0
relevant quantities from the drawings and appropriately
complete the bill of quantities. Any items required to be
installed that are not listed, must be listed with a cost
put against each item.
1.5 | Allowance for any costs associated with the requirements of the Principal Contractor | Sum | 1 |  | 0
Principal Contract preliminaries which may affect the selected sub-contract.
1.6 | Provide a project specific Health and Safety File in line with the | Sum | 1 |  | 0
End-User Client specifications including fall protection plans when working
at heights above 3m.
ENGINEERING AND MANAGEMENT
1.7 | Duties of the sub-contractor's staff. | Sum | 1 |  | 0
1.8 | Programming of the Works. | Sum | 1 |  | 0
1.9 | Equipment submittals, shop drawings approvals, cutting lists, | Sum | 1 |  | 0
samples of materials or equipment and construction drawings.
1.1 | Making reference, to other relevant drawings e.g. Civil, Structural, Architectural,
Structural, Electrical and Mechanical as well as any existing services etc.
1.11 | Tests and Inspection and commissioning | Sum | 1 |  | 0
1.12 | Setting out. | Sum | 1 |  | 0
1.13 | Free Maintenance and Guarantee for 12 Months incl quarterly service | Sum | 1 |  | 0
1.14 | Sundries | Sum | 1 |  | 0
1.15 | As built documentation | Sum | 1 |  | 0
1.16 | Training of appointed End-user client staff regarding the operation of | Sum | 1 |  | 0
specialised material or equipment, Fixed Automatic Sprinklers, Fire Detection
& Alarm, Smoke Ventilators, etc. as applicable.
| TOTAL SECTION 1 C/F TO TENDER SUMMARY |  |  |  | 0
SECTION 2
SPRINKLER SYSTEM
2.1 | WATER STORAGE TANKS
| Supply and install a bi-sectional combined sprinkler and conventional fire water tank of total total effective capacity of 344m3 to structural engineer's details and specifications. | No. | 1 |  | 0
Including all fittings
2.2 | SPRINKLER BOOSTER PUMPS
| Supply and install 1 x electrical duty, plus jockey pump and standby diesel driven sprinkler pump set complete with | Set | 1 |  | 0
all pumphouse piping and fittings including dry run protection, electrical control panels, valves in accordance with the
good practice guide of ASIB 12th edition of 2021.
Pump Duty
- 1800L/min @ 6-8 bar (Main electric and diesel driven pump)
- 120 L/min @ 7bar (Jockey)
2.3 | CONVENTIONAL FIRE BOOSTER PUMPS
| Supply and install duty and standby electrical pumps plus jockey complete with complete with all pump house | Set | 1 |  | 0
interconnecting piping and fittings including dry run protection, electrical control panels, valves, etc
good practice guide of ASIB 12th edition of 2021.
Pump Duty
- 2500 L/min @ 6 bar (duty and standby pumps)
- 90 L/min @ 6 bar (Jockey)
2.4 | SPRINKLER INSTALLATION CONTROL VALVE (ICV) ASSEMBLY
Each control valve described hereunder shall consist of but not limited to the following:
- Isolating Stop Valves
- A water motor alarm and gong
- Two pressure gauges located on either side of the alarm valve
- 15mm test pipe
- Ø50mm flushing connection
- Two Ø65mm instantaneous Fire Brigade booster connections
- Non-return valve if required
- Downstream and Upstream stop valves shall be monitored
2.4.1 | Ø150mm Sprinkler Control Valve assembly, including bypass arrangement, | No | 3 |  | 0
alarm gong, gauges, flow switch and required fittings and supports
2.4.1 | Ø100mm Sprinkler Control Valve assembly, including bypass arrangement, | No | 1 |  | 0
alarm gong, gauges, flow switch and required fittings and supports
2.5 | SPRINKLER SUPPLY MAINS - FROM ICV TO SPRINKLER ARRAY
INCLUDING HANGERS, FITTINGS AND SUPPORTS
All sprinkler piping shall be medium grade black steel piping to SANS 62-1
or BS1387, and the rates supplied herein shall include all pipe hangers,
supports, sockets, fittings nipples, flexible connections, and all necessary fittings
along the running length.
All piping will be applied with one coat of primer at the workshop prior to delivery to site and
then followed by another touch up of the primer on delivery to site. All exposed piping shall be
painted with two coats of signal red acrylic / gloss enamel paint.
Threaded pipe fittings up to and including 150mm diameter will be malleable cast iron to
SABS 509/1975 or BS 143/1952. Flanges up to and including 150mm diameter will be steel
plate flanges to SABS 1123/1600/4 or BS 4505/16/4. Welded pipe fittings up to and including.
300mm diameter will be of steel butt-weld type to JIS B2304-72. Weld flanges between
100mm and 300mm diameter will be steel plate flanges to SABS 1123/1600/3 or
BS 4504/16/3. “Klambon” couplings can be used where deemed necessary.
2.5.1 | Ø150 mm | m | 1500 |  | 0
2.5.2 | Ø100 mm | m | 750 |  | 0
2.5.3 | Ø80 mm | m | 450 |  | 0
2.5.4 | Ø65 mm | m | 600 |  | 0
2.6 | SPRINKLER HEADS
NOTE: The rate for sprinkler heads shall include all range pipes, i.e. 25mm, 32mm, 40mm and 50mm
2.6.1 | Supply & installation of Ø15mm, 68°C, Conventional type, Chrome pendant Fast Response fusible bulb | No | 1700 |  | 0
K8, 5,0 mm/min density ceiling level sprinklers complete with rosette.
2.6.2 | Supply & installation of Ø15mm, 68°C, brass upright, Fast Response | No | 1100 |  | 0
K8, 5,0 mm/min density to office void.
2.6.3 | Supply & installation of Ø15mm, 68°C, Conventional type Chrome pendant Standard Response fusible bulb | No | 1 |  | Rate Only
K8, 5,0 mm/min density to office void.
2.6.4 | Supply & installation of Ø15mm, 68°C, brass upright, Standard Response | No | 1 |  | Rate Only
K8, 5,0 mm/min density to office void.
REMOTE TEST VALVES
2.7 | Allow for the installation of remote test valves in specified areas. | No. | 8 |  | 0
SPARE PARTS
2.8 | Spare parts as listed in the ASIB specifications | Set | 1 |  | 0
ASIB INSPECTIONS
2.9 | Allow for ASIB inspections | No. | 1 |  | 0
2.1 | ITEMS NOT LISTED BUT NECESSARY FOR THE SUCCESSFUL COMPLETION OF
THE FIXED AUTOMATIC SPRINKLER FIRE-FIGHTING INSTALLATION
2.10.1 | Please specify: | No
2.10.2 | Please specify: | No
2.10.3 | Please specify: | No
| TOTAL SECTION 2 C/F TO TENDER SUMMARY |  |  |  | 0
SECTION 3
CONVENTIONAL FIRE PROTECTION SYSTEM
FIRE FIGHTING EQUIPMENT
FIRE HYDRANTS
Suction Hydrant
3.1 | Supply and install Right Angle Tamperproof Hydrant with 100mm Storz Outlet and | No. | 1 |  | 0
100mm Female BSP Inlet. (Installation downstream of water meter connection).
Backflow Preventer
3.2 | Supply and install Cast Iron Wafer Check Valve with Ductile Iron or 316 Stainless Steel | No. | 1 |  | 0
Double Doors and EPDM Seal. This valve assembly to be encased in a medium grade
600mm x 480mm manhole with frame for access for maintenance.
Twin Fire Brigade Booster Connection
3.3 | Supply and install Two-Port Booster with 65mm Brass Booster Connectors and a | No. | 1 |  | 0
Pressure Gauge and 100mm T/16 Inlet encased in a steel cover with front open. Pressure
gauge Dial to read up to 2500kPa. (Installed downstream of Item Above).
3.4 | Supply and install complete, internal 80mm x 65mm tamperproof fire hydrants with single lug | No | 18 |  | 0
FIRE HOSE REELS
3.5 | Supply and install 30 Metre Hose Reel complete with 25mm Chromium plated | No. | 37 |  | 0
Shut-off valve, Aluminium Nozzle, Hose Guide and angle iron fixing bracket.
PORTABLE FIRE EXTINGUISHERS
3.6 | Supply and install 9kg Dry Chemical Powder (DCP) Type portable fire extinguisher | No. | 20 |  | 0
complete with steel mounting bracket and 100mm W x 600mm L polished & varnished
Meranti Hardwood Backing board plugged in wall behind.
3.7 | Supply and install 4.5kg Dry Chemical Powder (DCP) Type portable fire extinguisher | No. | 74 |  | 0
complete with steel mounting bracket and 100mm W x 600mm L polished & varnished
Meranti Hardwood Backing board plugged in wall behind.
3.8 | Supply and install 5.0kg Carbon Dioxide (CO2) Type portable fire extinguisher | No. | 20 |  | 0
complete with steel mounting bracket and 100mm W x 600mm L polished & varnished
Meranti Hardwood Backing board plugged in wall behind.
STATUTORY SIGNAGE
3.9 | Photoluminescent signage and warning notices in accordance with SANS 1186 | No. | 150 |  | 0
Parts 1 & 5 incorporating the pictographs in the standard 190mm x 190mm module size
encased in Aluminium metal frames with chamfered edges mechanically and securely
fixed to walls or roof slabs. Strictly no double sided tape or silicone sealing of statutory
signage is allowed.
PIPING RETICULATION
All rates supplied in this bill of quantities will be deemed to include scaffolding to
any height and fixing piping up to roof height.
All piping rates supplied shall include couplings, bends, tees, sockets, pipe supports,
anchors, along the running length and backfilling and compaction where pipes are
laid in the ground.
All pipes suspended from concrete slabs, roof, ceiling, etc, shall be deemed to include
in the rates all necessary hanger brackets, threaded rods (irrespective of the
suspension length), nuts, washers, anchors and drilling of holes in the concrete slab.
All pipes are generally to be concealed inside ducts, ceiling voids except where it is
necessary to feed an appliance and fixed with standard type pipe supports and
brackets spaced at intervals strictly as per manufacturer's recommendations.
ABOVE GROUND PIPING
Galvanised Steel Pipework and Fittings
All above-ground firewater pipes shall be Medium Grade Galvanised Steel to SANS 62
Part 1 for nominal sizes from 25mm up to and including 150mm above which pipes shall
be Heavy Grade Galvanised Steel to SANS 719.
All pipes and fittings shall bi installed strictly in accordance with the manufacturer's
specifications, and recommendations.
Pipes shall be colour coded in accordance with the requirements of SANS 10140
Identification Colour Marking - Part 3: 2017 Contents of Pipelines or similar approved in
close consultation with the engineer.
Medium Grade Steel Pipes
3.1 | 100mm diameter pipes | m | 700 |  | 0
3.11 | 80mm diameter pipes | m | 15 |  | 0
3.12 | 50mm diameter pipes | m | 1400 |  | 0
3.13 | 40mm diameter pipes | m | 10 |  | 0
3.14 | 32mm diameter pipes | m | 20 |  | 0
3.15 | 25mm diameter pipes | m | 250 |  | 0
BELOW GROUND EXTERNAL PIPING (BY OTHERS)
High Pressure uPVC Class 16 pipes and fittings to SANS 966 Part 1: 2019 suitable for
below-ground applications for the conveyance of potable water in reticulation
systems in which continuous temperatures in excess of 25˚C are not encountered
3.17 | Ø160mm High pressure pipe laid in ground not exceeding 1000mm deep. | m | 1 | Rate only
3.18 | Ø110mm High pressure pipe laid in ground not exceeding 1000mm deep. | m | 1 | Rate Only
3.19 | Ø75mm High pressure pipe laid in ground not exceeding 1000mm deep. | m | 1 | Rate Only
3.2 | ITEMS NOT LISTED BUT NECESSARY FOR THE SUCCESSFUL COMPLETION OF
CONVENTIONAL FIRE PROTECTION INSTALLATION
3.20.1 | Please specify: | No
3.20.2 | Please specify: | No
3.20.3 | Please specify: | No
| TOTAL SECTION 3 C/F TO TENDER SUMMARY |  |  |  | 0
SECTION 4
ATRIUM SMOKE CONTROL
Allow for design, supply and installation of an EN 12101 compliant smoke control system for the Atrium area of the building
4.1 | Smoke ventilation fans - Allow for BS EN 12101-3 tested smoke ventilation fans complete with accessories. 300° C fire rated for 2 hours. 7,5m³/s@200Pa | No | 4 |  | 0
4.2 | BS EN 12101-3 tested smoke ventilation fans complete with accessories. 300° C fire rated for 2 hours. 15m³/s@200Pa | No | 2 | Rate only
4.3 | PH120 fire rated cable 4 Core | m | 140 |  | 0
4.3 | Single Zone Master Control Panel for 2 Fans including power supply unit | No | 1 |  | 0
4.4 | Atrium Fire Curtains - Allow for BS 8524 compliant fire curtains for the atrium
| 5m wide with 3,5m drop and smoke seals. These to be total fail safe by gravity in the event of total wiring, short circuit and/or system corruption | No | 30 |  | 0
4.5 | Motor Control units | No | 30 |  | 0
4.6 | Power supply unit - 24V | No | 5 |  | 0
4.6 | Window Actuators - EN12101-2 compliant Including all accessories | No | 6 |  | 0
| TOTAL SECTION 4 C/F TO TENDER SUMMARY |  |  |  | 0
SECTION 5
FIRE SEALING
5.1 | FIRE SEALING - Allow for fire sealing of penetrations through fire walls , service ducts and floor to floor slabs. | Sum | 1 |  | 0
| TOTAL SECTION 4 C/F TO TENDER SUMMARY |  |  |  | 0